## Slide 1: ACLAD Operations Status
7 May 2022

## Slide 2: ACLAD STATUS
CURRENTLY PUMPING 89,000 GALLONS PER DAY
Drilled and developed well #4
  Installing pump in progress
Replace pump at Well #1 (Narcissa-Ginger root)
Replaced pump at well #15 (Narcissa-Vanderlip)
Replaced pump at well #19 (end of Narcissa)
Re-developing well #3 (mid-Figtree)
ACLAD Near-term Plan
  Well Drilling Plan: Well #7, Well #6
PVDS Systems Output Meter

## Slide 3: Schraiber lessons
Cycle pumps < 6 times per hr, Run < 6-8 hrs then 1 hr rest
Add check valve near pump to reduce head pressure at start up
  No weep holes
Add cooling sleeve around motor to cool motor and filter water
Discharge pipe: > 300’= 1.25”, <300’ = 1”
Pumps designed for clean water, dirty water = shorter life
Mount pumps 5’-10’ above well bottom or above mud
Do not run dry, use pump saver (Pump tech)

## Slide 5
ACLAD Summary Report June 7, 2022
Chart: 
| 44571 | 44572 | 44586 | 44594 | 44600 | 44607 | 44614 | 44621 | 44628 | 44635 | 44642 | 44649 | 44656 | 44663 | 44670 | 44677 | 44684 | 44691 | 44698 | 44705 | 44712 | 44719
Narcissa/Gingerroot 1 | 20863.0714 | 21829.5714 | 13171.4286 | 7020 | 17153.3333 | 6381.4286 | 0 | 20680 | 17455.6522 | 17178.5714 | 19208.5714 | 18492.8571 | 17631.4286 | 17214.2857 | 16892.8571 | 5751.4286 | 0 | 28664.2857 | 12554.25 | 13691.5 | 17063.5714 | 13708.4286
lower Narcissa 2 | 5108.5714 | 5004.2857 | 5014.2857 | 4977.1429 | 5526.6667 | 5100 | 5948.5714 | 2051.4286 | 4944.2857 | 4351.4286 | 4140 | 3998.5714 | 4207.1429 | 4230 | 4600 | 4925.7143 | 5088.5714 | 20092.8571 | -8662.8571 | 5520 | 5200 | 3604.2857
Beanfield 11 | 11344.7143 | 11402.5714 | 11142.8571 | 10955 | 10805 | 10871.5714 | 11198.7143 | 9065.7391 | 11665.4286 | 11014 | 11916.8571 | 0 | 23839.8571 | 11733.2857 | 11093.1429 | 11144.8571 | 11433.2857 | 15164.8571 | 3827.2857 | 11194.2857 | 11221.2857 | 6348.4286
upper Gingerroot 12 | 17531.4286 | 17685.7143 | 16897.8571 | 14955.7143 | 20133.3333 | 16454.2857 | 15795.7143 | 17100.8696 | 17227.1429 | 16504.2857 | 17342.8571 | 17265.7143 | 17342.8571 | 17018.5714 | 13750 | 0 | 12902.8571 | 29344.2857 | 27571.4286 | 29075.7143 | 24934.2857 | 25632.8571
King/Sweetbay 13 | 9997.1429 | 10087.1429 | 9845 | 7271.25 | 12960 | 9712.8571 | 10105.7143 | 3455.6522 | -5872.8571 | 0 | 0 | 11943.2857 | 2888.1429 | 9184.4286 | 14065.1429 | 14014.1429 | 14206.4286 | 13698.4286 | 13675.2857 | 13610 | 13589.7143 | 13212.1429
Narcissa/Vanderlip 15 | 1779.5714 | 1750.1429 | 1786.1429 | 3206 | 15472.3333 | 13292 | 0 | 12623.6522 | 21339.7143 | 9467.1429 | 14610.5714 | 7789 | 11133.8571 | 11659.8571 | 11625.8571 | 11659.5714 | 6035 | 951.4286 | 5.1429 | -5.1429 | 7885.1429 | 8500
Petak/Sweetbay 16 | 6590 | 7081.4286 | 9236.4286 | 9235 | 8160 | 12240 | 5170 | 8450.4348 | 8801.4286 | 9518.5714 | 11954.2857 | 9125.7143 | 8264.2857 | 13804.2857 | 7061.4286 | 9941.4286 | 11528.5714 | 10561.4286 | 9595.7143 | 4777.1429 | 7344.2857 | 14935.7143
Thyme 17 | 1267.8571 | 1001.4286 | 952.8571 | 941.25 | 911.6667 | 905.7143 | 990 | 944.3478 | 868.5714 | 857.1429 | 851.4286 | 844.2857 | 857.1429 | 848.5714 | 842.8571 | 835.7143 | 858.5714 | -152.8571 | 400 | 2191.4286 | 802.8571 | 3454.2857
End of Narcissa 19 | 2570.7143 | 2144.2857 | 2108.5714 | 1638.5714 | 1900 | 1427.1429 | 1317.1429 | 1109.5652 | 794.2857 | 580 | 157.1429 | 0 | 0 | -1.4286 | 1238.5714 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sweetbay Yamaguchi | 3961.4286 | 3825.7143 | 3851.4286 | 3818.75 | 3618.3333 | 3700 | 3582.8571 | 4266.087 | 3494.2857 | 3377.1429 | 3431.4286 | 3452.8571 | 3372.8571 | 11984.2857 | 23298.5714 | 17594.2857 | 0 | 0 | 0 | 0 | 0 | 0
Lower Figtree 3 | 9602.1429 | 10057.1429 | 8330.7143 | 7102.8571 | 7851.6667 | 5637.1429 | 5240 | 3880 | 3845.7143 | 1562.8571 | 0 | 0 | 4302.8571 | 3798.5714 | 1677.1429 | 4504.2857 | 3108.5714 | 2595.7143 | 1440 | 302.8571 | 524.2857 | 0
Mid Sweetbay 8 | -1 | 0 | 2090 | 5720 | 1401.6667 | 1390 | 1397.1429 | 693.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Slide 6: Weekly Well Monitoring (gallons per day)
 | Narcissa/Gingerroot | lower Narcissa | Beanfield | upper Gingerroot | King/Sweetbay | Narcissa/Vanderlip
 | 1 | 2 | 11 | 12 | 13 | 15
Petak/Sweetbay | Thyme | End of Narcissa | Sweetbay | Lower Figtree | Mid Sweetbay | Total GPD | PVDS Meter
16 | 17 | 19 | Yamaguchi | 3 | 8 |  | 
3-May | 0 | 5,089 | 11,433 | 12,903 | 14,206 | 6,035
10-May | 28,664 | 20,093 | 15,165 | 29,344 | 13,698 | 951
17-May | 12,554 | -8,663 | 3,827 | 27,571 | 13,675 | 5
24-May | 13,692 | 5,520 | 11,194 | 29,076 | 13,610 | -5
31-May | 17,064 | 5,200 | 11,221 | 24,934 | 13,590 | 7,885
7-Jun | 13,708 | 3,604 | 6,348 | 25,633 | 13,212 | 8,500
3-May
10-May
17-May
24-May
31-May
7-Jun
859 | 0 | 0 | 3,109 | 0 | 62,053 | 98,494 | 98,494
-153 | 0 | 0 | 2,596 | 0 | 118,325 | 92,391 | 92,391
400 | 0 | 0 | 1,440 | 0 | 58,966 | 71,043 | 71,043
2,191 | 0 | 0 | 303 | 0 | 80,055 | 68,171 | 68,171
803 | 0 | 0 | 524 | 0 | 88,041 | 89,600 | 89,600
3,454 | 0 | 0 | 0 | 0 | 89,396 | 76,686 | 76,686